Software USB communication controller

for UPS PowerCom Smart KING Pro series for model

SKP-500A, SKP-700A, SKP-1000A, SKP-1250A, SKP-1500A, SKP-2000A

Developer of software

research-and-production company "MES-s.r.l."

Release 1.3

Mai, 23, 2008

Revision History

| Ver | Date | Description | Modify by |
| --- | --- | --- | --- |
| 1.0 | 24.04.2008 | New project | MES-s.r.l |
| 1.1 | 14.05.2008 | Correction | MES-s.r.l |
| 1.2 | 23.05.2008 | Definitive edition | MES-s.r.l., R.Ahmetzeanov |
|  |  | Concurred by | PowerCom ……………… |
| 1.3 | 27.10.2008 | Final | MES-s.r.l, |

Table of Contents

1.	Introduction	3

2.	POWERCOM Communication Protocols for UPS SKP series for models SKP-500A, SKP-700A, SKP-1000A, SKP-1250A, SKP-1500A, SKP-2000A	3

3.	Description of the HID Reports for PowerCom UPS-USB interface Smart KING series	8

3.	Data for Usage from UART of Power Devices PowerCom and constants.	12

4.	Data for calculation of parametres in the table of time RunTimeToEmpty.	18

5.	Conditions for setting  Present Status.	19

### Introduction

Software USB communication controller for UPS PowerCom Smart KING Pro series for model SKP-500A, SKP-700A, SKP-1000A, SKP-1250A, SKP-1500A, SKP-2000A it is developed on the basis of POWERCOM UART Communication Protocols (Megatec) for UPS SKP series.

### POWERCOM Communication Protocols for UPS SKP series for models SKP-500A, SKP-700A, SKP-1000A, SKP-1250A, SKP-1500A, SKP-2000A

A. General: This section specifies the UART communication protocol with main processor UPS.

B. Hardware:

Baud rate……………….. :  2400bps

Data length………………:  8 bit

Stop bits…………………:  1 bit

Parity…………………….:  None

C. Communication Protocol:

- Status Inquiry 1

Computer	: Q1<CR>

UPS	: UPS status data stream (55 bytes), such as (MMM.M NNN.N PPP.P QQQ RR.R S.SS TT.T b7b6b5b4b3b2b1b0<CR>

UPS status data stream: There should be a space character between every field for data separation. M, N, P, S is and integer number

ranging from 0 to 9. The unit is Volt. The meaning of each field is list as followed:

a. Start byte		: (

b. I/P voltage		: MMM.M

c. I/P fault voltage	: NNN.N

d. O/P voltage		: PPP.P

e. O/P current		: QQQ, QQQ is a percent of maximum current, not an absolute value.

f. I/P frequency	: RR.R, R is an integer number ranging from 0 to 9. The unit is Hz.

g. Battery voltage	: SS.S or S.SS, S is an integer number ranging from 0 to 9.

For on-line units actual battery voltage is provided in the form S.SS

For standby units actual battery voltage is provided in the form SS.S

UPS type in UPS status will determine which reading was obtained.

h. Temperature	: TT.T, T is an integer number ranging form 0 to 9. The unit is degree of centigrade.

i. UPS Status		: b7b6b5b4b3b2b1b0, Where bn is a ASCII character ‘0’ or ‘1’.

| Bit | Description |
| --- | --- |
| b7 | 1 : Utility Fail (Immediate) |
| b6 | 1 : Battery Low |
| b5 | 1 : Bypass/Boost Or Buck Active (AVR on) |
| b4 | 1 : UPS Failed |
| b3 | 1 : UPS Type In Progress (0 is On-Line) |
| b2 | 1 : Test In Progress |
| b1 | 1 : Shutdown Active |
| b0 | 1 : Beeper On |

j. Stop Byte		: <CR>

Example. Computer   : Q1<CR>

UPS   : (208.4 140.0 208.4 034 59.9 2.05 35.0 00110000<CR>

- Status Inquiry 2

Computer	: DQ1<CR>

UPS	: UPS status data stream (55 bytes)

(MMM.M NNN.N PPP.P QQQ RR.R AAAA TT.T b7b6b5b4b3b2b1b0<CR>

Such as Status Inquiry 1 except of AAAA - Remaining Capacity of Battery. A is an integer number ranging from 0 to 9. The unit is percent.

Example. Computer   : DQ1<CR>

UPS   : (208.4 140.0 208.4 034 59.9 0100 35.0 00110000<CR>

- Test for 10 seconds

Computer	: T<CR>

UPS	: Test for 10 seconds and return to utility. If battery low occurs during testing, UPS will return to utility immediately.

- Test until battery low

Computer	: TL<CR>

UPS	: Test until battery low and return to utility.

- Test for specified time period

Computer	: T< n><CR>

UPS	: Test for <n> minutes. <n> is a number ranging from 01 to 99. During testing, UPS returns to utility immediately, if battery low occurs.

- Turn On/Off beep – Toggle the UPS beeper

Computer	: Q<CR>, when the AC power failed, UPS will generate a warning beep to inform the manager. Manager could toggle the warning beep by

sending this command.

- Shutdown Command

Computer	: S<n><CR>

UPS	: Shut UPS output off in <n> minutes.

a. The UPS output will be off in <n> minutes, even if the utility power is present.

b. If the battery low occurs before <n> minutes, the output is turned off immediately.

c. After UPS shutdown, the controller of UPS monitors the utility power. If the utility is recovered, the UPS will wait for 10 seconds and connect the utility to output.

d. <n> is a number ranging from .2, .3, …, 01, 02,…, up to 10.

Example.  S.3<CR> - shut output off in 0.3 minutes

- Shutdown and Restore Command

Computer	: S<n>R<m><CR>

UPS	: Shut UPS output off in <n> minutes. Waiting for <m> minutes, then turn on UPS output again.

a. The shutdown sequence is the same as the previous command. When the <m> minutes expired, the utility do not restore, the UPS will wait until utility restore.

b. If UPS is in restore waiting state, the “C” command can let the shutdown procedure cancelled.

c. If UPS is in restore waiting state, the “C” command can let the UPS output turned on, but UPS must be hold off at least 10 seconds (if utility is present).

d. <n> is a number ranging from .2, .3,…, 01, 02,…, up to 10.

e. <m> is a number ranging from 0001 to 9999.

Example.  S.5R0060<CR> - shut output off in 0.5 minutes (30 seconds) then turns on output in 60 minutes.

- Cancel Shutdown Command:

Computer	: C<CR>

UPS	: Cancel the  S<n><CR>  and  S<n>R<m><CR>  command.

a. If UPS is in shutdown waiting state, the shutdown command is cancelled.

b. If UPS is in restore waiting state, the UPS output is turned on, but UPS must be hold off at least 10 seconds (if utility is present).

- Cancel Test Command:

Computer	: CT<CR>

UPS	: Cancel all test activity and connect the utility to output immediately.

11. UPS Information Command:

Computer	: I<CR>

UPS	: #Company_Name UPS_Model Version<CR>. There should be a space character between every field for separation.

This function will make the UPS respond with the basic information about the company who manufacture the UPS, the model name of the

UPS and the version number of the UPS firmware. The length of every field is listed as follows:

Company_Name	: 15 characters, leave space if less than 15 characters

UPS_Model		: 10 characters, leave space if less than 10 characters

Version		: 10 characters, leave space if less than 10 characters

Example. Computer   : I<CR>

UPS   : #POWERCOM        SKP-500A   S505-V1.80<CR>

12. UPS Rating Information:

Computer	: F<CR>

UPS	: #MMM.M QQQ SS.SS RR.R<CR>

This function makes the UPS answer the rating value of UPS. There should be a space character between every field for separation. The UPS’s response contains the following information field:

MMM.M		: Rating Voltage

QQQ			: Rating Current

SS.SS or SSS.S  	: Battery Voltage

RR.R			: Frequency

Example. Computer   : F<CR>

UPS   : #220.0 002 12.00 50.0<CR>

13. Display AVR voltage :

Computer	: V<CR>

UPS	: PPP QQQ MMM RRR SSS<CR>

This function forces UPS to show boundary values of a voltage for change of an operating mode. There should be a space character between every field for separation. The UPS’s response contains the following information field:

PPP		: Low Voltage Transfer to battery backup

QQQ		: Low Voltage Transfer to AVR

MMM  	: Nominal (rating) Voltage

RRR		: High Voltage Transfer to AVR

SSS		: Low Voltage Transfer to battery backup

Example. Computer   : V<CR>

UPS   : 165 200 220 240 275<CR>

C. Command summary:

Table 1.

| Item | Command | Description | Example of the received data from UPS |
| --- | --- | --- | --- |
| 1 | Q1 | Status inquiry | (228.0 228.0 228.0 000 50.0 13.8 32.0 00000001 |
| 2 | DQ1 | Status inquiry | (228.0 228.0 228.0 000 50.0 0100 32.0 00000001 |
| 3 | T | 10 seconds test |  |
| 4 | TL | Test until battery low |  |
| 5 | T<n> | Test for specified time period |  |
| 6 | Q | Turn on/off beep |  |
| 7 | S<n> | Shut down command |  |
| 8 | S<n>R<m> | Shut down and Restore command |  |
| 9 | C | Cancel Shut down command |  |
| 10 | CT | Cancel Test command |  |
| 11 | I | UPS Information command | #POWERCOM SKP-500A S505-V1.80 |
| 12 | F | UPS rating information | #220.0 002 12.00 50.0 |
| 13 | V | Display AVR voltage | 165 200 220 240 275 |

### Description of the HID Reports for PowerCom UPS-USB interface Smart KING series

Table 2.

| Report Number | Page, Usage ID | Usage Name | Data Access |
| --- | --- | --- | --- |
|  | 8404 | UPS COLLECTION (Application) |  |
|  | 8424 | PowerSummary COLLECTION (Logical) |  |
| 1 | 84FE | IProduct | R/O |
| 2 | 84FF | ISerialNumber | R/O |
| 3 | 84FD | IManufacturer | R/O |
| 4 | 858F | iOEMInformation | R/O |
| 5 | 8589 | iDeviceChemistery | R/O |
| 7 | 858B | Rechargable | R/O |
| 8 | 852C | CapacityMode | R/O |
| 9 | 8583 | DesignCapacity * | R/O |
|  | 8567 | FullChargeCapacity * |  |
| 10 | 8566 | RemainingCapacity | R/O |
| 11 | 858C | WarningCapacityLimit | R/O |
| 12 | 8529 | RemainingCapacityLimit | R/W |
| 13 | 8585 | ManufacturerDate | R/O |
| 14 | 8568 | RunTimeToEmpty | R/O |
| 15 | 8457 | DelayBeforeShutdown | R/W |
| 16 | 8456 | DelayBeforeStartup | R/W |
| 17 | 8440 | ConfigVoltage | R/O |
| 40 | 8453 | LowVoltageTransfer (to AVR) | R/O |
| 41 | 8454 | HighVoltageTransfer (to AVR) | R/O |
| 42 | 8453 | LowVoltageTransfer (to battery backup) | R/O |
| 43 | 8454 | HighVoltageTransfer (to battery backup) | R/O |
| 18 | 8430 | Voltage | R/O |
| 44 | 8436 | Temperature | R/O |
| 19 | 845A | AudibleAlarmControl | R/W |
| 20 | 8402 | PresentStatus COLLECTION (Logical) | R/O |
|  |  | Collection multi-bits Report ** |  |
|  | 8544 | Charging |  |
|  | 8545 | Discharging |  |
|  | 85D0 | ACPresent |  |
|  | 85D1 | BatteryPresent |  |
|  | 8542 | BelowRemainingCapacityLimit ** |  |
|  | 8543 | RemainingTimeLimitExpired ** |  |
|  | 854B | NeedReplacement |  |
|  | 85DB | VoltageNotRegulated ** |  |
|  | 8468 | ShutdownRequested ** |  |
|  | 8469 | ShutdownImminent |  |
|  | 8473 | CommunicationLost |  |
|  | 8465 | Overload |  |
|  |  | COUNT (3) ** |  |
|  | 8680 | Usage (80) from Usage_Page (86) ** |  |
|  |  | END_COLLECTION [PresentStatus, Logical] |  |
|  |  | END_COLLECTION [PoweSummary, Logical] |  |
|  | 8412 | Battery COLLECTION (Physical) |  |
| 21 | 8458 | Test | R/W |
| 22 | 8470 | Initialized | W/O |
| 23 | 8585 | ManufacturerDate | R/O |
| 24 | 8566 | RemainingCapacity | R/O |
| 25 | 8440 | ConfigVoltage | R/O |
| 26 | 8430 | Voltage | R/O |
| 27 | 8456 | DelayBeforeStartup | R/W |
| 45 | 8436 | Temperature | R/O |
|  |  | END_COLLECTION [Battery, Physical] |  |
|  | 841A | Input COLLECTION (Physical) |  |
| 28 | 8440 | ConfigVoltage | R/O |
| 29 | 8430 | Voltage | R/O |
| 46 | 8430 | Voltage (fault) | R/O |
| 30 | 8432 | Frequency | R/O |
|  |  | END_COLLECTION [Input, Physical] |  |
|  | 841C | Output COLLECTION (Physical) |  |
| 47 | 8441 | ConfigCurrent | R/O |
| 31 | 8435 | PercentLoad | R/O |
| 32 | 8440 | ConfigVoltage | R/O |
| 33 | 8430 | Voltage | R/O |
| 48 | 8442 | ConfigFrequency | R/O |
| 34 | 8432 | Frequency | R/O |
| 35 | 8457 | DelayBeforeShutdown | R/W |
| 36 | 8456 | DelayBeforeStartup | R/W |
|  |  | END_COLLECTION [Output, Physical] |  |
| 6 | 8401 | Iname | R/O |
| 37 | 845A | Audible Alarm Control | R/W |
| 38 | 8402 | Present Status COLLECTION (Logical) | R/O |
|  |  | Collection multi-bits Report |  |
|  | 8544 | Charging |  |
|  | 8545 | Discharging |  |
|  | 85D0 | ACPresent |  |
|  | 85D1 | BatteryPresent |  |
|  | 8542 | BelowRemainingCapacityLimit ** |  |
|  | 8543 | RemainingTimeLimitExpired ** |  |
|  | 854B | NeedReplacement |  |
|  | 85DB | VoltageNotRegulated ** |  |
|  | 8468 | ShutdownRequested ** |  |
|  | 8469 | ShutdownImminent |  |
|  | 8473 | CommunicationLost |  |
|  | 8465 | Overload |  |
|  | 846E | Boost |  |
|  | 846F | Buck |  |
|  | 8471 | Tested |  |
|  | 8680 | Usage(80) from Usage_Page (86) ** |  |
|  |  | END_COLLECTION [PresentStatus, Logical] |  |
| 39 | 8469 | ShutdownImminent | W/O |
|  |  | END_COLLECTION [UPS, Application] |  |

*)   - Two Usage in one report.

**) - Not to use. For compatibility with system (APC-based) driver.

### Data for Usage from UART of Power Devices PowerCom and constants.

Table 3. System requests for usage with Microsoft UPS system driver (first Byte is Byte 0 )

| Report Number | Page, Usage ID | Usage Name | Data Access | Data | Length |
| --- | --- | --- | --- | --- | --- |
|  | 8424 | PowerSummary COLLECTION |  |  |  |
| 1 | 84FE | iProduct**** | R/O | From command “I”, UPSModel | 40 Byte |
| 2 | 84FF | iSerialNumber**** | R/O | 0A3-0000-0001 | 32 Byte |
| 3 | 84FD | iManufacturer**** | R/O | From command “I”, CompanyName | 30 Byte |
| 4 | 858F | iOEMInformation**** | R/O | From command “I”, CompanyName | 30 Byte |
| 5 | 8589 | iDeviceChemistery**** | R/O | PbAc | 10 Byte |
| 7 | 858B | Rechargable | R/O | Constant, value=1 | 1 Byte |
| 8 | 852C | CapacityMode | R/O | Constant, value=2 (%) | 1 Byte |
| 9 | 8583 | Designcapacity* | R/O | Constant, value=100 (in %) | 2 Byte |
|  | 8567 | FullChargeCapacity * |  | Constant, value=100 (in %) |  |
| 10 | 8566 | RemainingCapacity | R/O | From command “DQ1”, Remaining Capacity of Battery | 1 Byte |
| 11 | 858C | WarningCapacityLimit | R/O | Constant, value=30 (in %) | 1 Byte |
| 12 | 8529 | RemainingCapacityLimit | R/W | Initially 10 (in %), is it hereinafter assigned by system driver | 1 Byte |
| 13 | 8585 | ManufacturerDate | R/O | ( Year-1980 ) * 512 + Month * 32 + Day | 2 Byte |
| 14 | 8568 | RunTimeToEmpty | R/O | It is calculated by commands “I” and “DQ1” ( in sec ) Calculated in table format on the basis of data table №4 T =( ( Caccum * K * BatteryLevel * 60 min ) / ( Pnom * * LoadLevel ) ) * 60 Takes places in a tabular format in memory of USB processor | 2 Byte |
| 15 | 8457 | DelayBeforeShutdown *** | R/W | Read: Value s - ShutDown status, where bit s0 - current UPS Status from command “DQ1”, b1 If b1=1 Then s0=1 (Shutdown Active ) bit s1 - Power state from command “DQ1”, b7 If b7=1 Then s1=1 (Power fail) at the moment of last SD/SD+WU command execution bit s2 - the command "S" was executed - “S<T[n]>“ bit s3 - the command "R" was executed - “S<T[n]>R<m>“ Write: Value n - index of the table T***** of possible delays If n = 0 Then command “C” If n = 1..18 Then If Power_Fail (b7=1) Then command “S<T[n]>“ Else command “S<T[n]>R<m>“, where mmm - value memorized in USB controller by DelayBeforeStartup command | 1 Byte |
| 16 | 8456 | DelayBeforeStartup *** | R/W | Read: Value mmmm – memorized value of Delay before Restore. This value was previously written from PC. Write: Value mmmm - Delay before Restore, minutes [1..99999]. This value memorized in USB controller and used later in DelayBeforeShutdown. | 4 Byte |
| 17 | 8440 | ConfigVoltage (nominal for AVR) | R/O | From command “V” | 2 Byte |
| 40 | 8453 | LowVoltageTransfer (to AVR) | R/O | From command “V” | 2 Byte |
| 41 | 8454 | HighVoltageTransfer (to AVR) | R/O | From command “V” | 2 Byte |
| 42 | 8453 | LowVoltageTransfer (to battery backup) | R/O | From command “V” | 2 Byte |
| 43 | 8454 | HighVoltageTransfer (to battery backup) | R/O | From command “V” | 2 Byte |
| 18 | 8430 | Voltage | R/O | From command “DQ1”, O/P_Voltage | 2 Byte |
| 44 | 8436 | Temperature | R/O | From command “DQ1”, Temperature | 1 Byte |
| 19 | 845A | AudibleAlarmControl | R/W | Read: If command “DQ1”, b0=1 Then value = 2 (enabled) If command “DQ1”, b0=0 Then value = 3 (muted) Write: command “Q”, value: 0=toggle, 1(3)=mute, 2=enable | 1 Byte |
|  | 8402 | Present Status COLLECTION |  |  |  |
| 20 |  | Collection multi-bits Report | R/O |  | 2 Byte |
|  | 8544 | Charging |  | From command “DQ1” If b7=0 and Battery_Level<100% Then value=1 (see table 5) |  |
|  | 8545 | Discharging |  | From command “DQ1” If b7=1 and Battery_Level>0% Then value=1 (see table 5) |  |
|  | 85D0 | ACPresent |  | From command “DQ1”, UPS Status If b7=0 Then value=1 |  |
|  | 85D1 | BatteryPresent |  | Constant, value=1 |  |
|  | 8542 | BelowRemainingCapacityLimit ** |  | From command “DQ1” (see table 5) |  |
|  | 8543 | RemainingTimeLimitExpired ** |  | From command “DQ1” If Battery_Level≤10% Then value=1 (see table 5) |  |
|  | 854B | NeedReplacement |  | From command “DQ1” If b6=0 and Battery_Level=0 Then value=1 |  |
|  | 85DB | VoltageNotRegulated |  | From command “DQ1”, UPS Status If b4=1 Then value=1 |  |
|  | 8468 | ShutdownRequested ** |  | Constant, value=0 |  |
|  | 8469 | ShutdownImminent |  | (see table 5) |  |
|  | 8473 | CommunicationLost |  | If ErrorUART Then value =1 |  |
|  | 8465 | Overload |  | From commands “DQ1” If O/P_current>100% Then value=1 |  |
|  |  | COUNT(3)** |  |  |  |
|  | 8680 | Usage(80) from Usage_Page (86) ** |  | Constant, value=0 |  |
|  | 8412 | Battery COLLECTION |  |  |  |
| 21 | 8458 | Test | R/W | Read: From command “DQ1”, UPS Status If b2=0, b4=0 Then value = 1 ( Done and Passed) If b2=0, b4=1 Then value = 3 ( Done and Error ) If b2=1 Then value = 5 ( Test in progress ) | 1 Byte |
|  |  |  |  | Write : If value =1 Then command “T” ( Quick test ) If value =2 Then command “TL” ( Deep test ) If value =3 Then command “CT” ( Abort test ) If value =4..102 Then command “T<value-3>” | 1 Byte |
| 22 | 8470 | Initialized | W/O | Write : If value =1 Then command “C” ( WakeUp ) If value =2 Then ( Reset ) If value =3 Then command “C” (WakeUp + Reset ) | 1 Byte |
| 23 | 8585 | ManufacturerDate | R/O | (see Report number 13) | 2 Byte |
| 24 | 8566 | RemainingCapacity | R/O | From command “DQ1”, Remaining Capacity of Battery | 1 Byte |
| 25 | 8440 | ConfigVoltage | R/O | From command “F”, Battery_Voltage | 2 Byte |
| 26 | 8430 | Voltage | R/O | From command “Q1”, Battery_Voltage | 2 Byte |
| 27 | 8456 | DelayBeforeStartup *** | R/W | (see Report number 16) | 3 Byte |
| 45 | 8436 | Temperature | R/O | (see Report number 44) | 1 Byte |
|  | 841A | Input COLLECTION |  |  |  |
| 28 | 8440 | ConfigVoltage | R/O | From command “F”, Rating_Voltage | 2 Byte |
| 29 | 8430 | Voltage | R/O | From command “DQ1”, I/P_voltage | 2 Byte |
| 46 | 8430 | Voltage (fault) | R/O | From command “DQ1”, I/P_fault_voltage | 2 Byte |
| 30 | 8432 | Frequency | R/O | From command “DQ1”, I/P_frequency | 1 Byte |
|  | 841C | Output COLLECTION |  |  |  |
| 47 | 8441 | ConfigCurrent | R/O | From command “F”, Rating_Current | 1 Byte |
| 31 | 8435 | PercentLoad | R/O | From command “DQ1”, O/P_current | 1 Byte |
| 32 | 8440 | ConfigVoltage | R/O | From command “F”, Rating_Voltage | 2 Byte |
| 33 | 8430 | Voltage | R/O | From command “DQ1”, O/P_voltage | 2 Byte |
| 48 | 8442 | ConfigFrequency | R/O | From command “F”, Rating_frequency | 2 Byte |
| 34 | 8432 | Frequency | R/O | From command “DQ1”, I/P_frequency | 1 Byte |
| 35 | 8457 | DelayBeforeShutdown *** | R/W | (see Report number 15) | 1 Byte |
| 36 | 8456 | DelayBeforeStartup *** | R/W | (see Report number 16) | 3 Byte |
| 6 | 8401 | iName**** | R/O | POWERCOM USB UPS | 34 Byte |
| 37 | 845A | Audible Alarm Control | R/W | (see Report number 19) | 1 Byte |
|  | 8402 | Present Status COLLECTION |  |  |  |
| 38 |  | Collection multi-bits Report | R/O |  | 2 Byte |
|  | 8544 | Charging |  | (see Report number 20) |  |
|  | 8545 | Discharging |  | (see Report number 20) |  |
|  | 85D0 | ACPresent |  | (see Report number 20) |  |
|  | 85D1 | BatteryPresent |  | (see Report number 20) |  |
|  | 8542 | BelowRemainingCapacityLimit ** |  | (see Report number 20) |  |
|  | 8543 | RemainingTimeLimitExpired ** |  | (see Report number 20) |  |
|  | 854B | NeedReplacement |  | (see Report number 20) |  |
|  | 85DB | VoltageNotRegulated |  | (see Report number 20) |  |
|  | 8468 | ShutdownRequested ** |  | (see Report number 20) |  |
|  | 8469 | ShutdownImminent |  | (see Report number 20) |  |
|  | 8473 | CommunicationLost |  | (see Report number 20) |  |
|  | 8465 | Overload |  | (see Report number 20) |  |
|  | 846E | Boost |  | From command “DQ1” If b5=1 and I/P_voltage<O/P_voltage Then value=1 |  |
|  | 846F | Buck |  | From command “DQ1” If b5=1 and I/P_voltage>O/P_voltage Then value=1 |  |
|  | 8471 | Tested |  | From command “DQ1”, UPS Status b2 |  |
|  | 8680 | Usage(80) from Usage_Page (86) ** |  | (see Report number 20) |  |
| 39 | 8469 | ShutdownImminent | W/O | Write: If value =2 and LoadLevel=0 Then command “S<2>” If value =0 Then command “C” | 1 Byte |

*)         - Two Usage in one report.

**)       - Not to use. For compatibility with system (APC-based) driver.

***)     - Does not correspond to the standard "Universal Serial Bus Usage Tables for HID Power Devices".

Productivity microcontroller CY7C63723 is not sufficient, that real-time to execute transformations data.

****)   - Strings are sent in format UNICOD

*****) - Table of possible delays for Shutdown commands

| Index | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Value | 12s | 18s | 24s | 30s | 36s | 42s | 48s | 54s | 1min | 2min | 3min | 4min | 5min | 6min | 7min | 8min | 9min | 10min |
| Sent to UPS | .2 | .3 | .4 | .5 | .6 | .7 | .8 | .9 | 01 | 02 | 03 | 04 | 05 | 06 | 07 | 08 | 09 | 10 |

### Data for calculation of parametres in the table of time RunTimeToEmpty.

Table 4.

| UPS_Model | UPS Information Command | Pnom (Wt) | DesignCapacity (A/H) | Number Acc. | Efficiency inverter (%) |
| --- | --- | --- | --- | --- | --- |
| SKP-500A | SKP-500A S505-V1.80 | 300W | 12V/7Ah | 1 | 65%~70% |
| SKP-700A | SKP-700A | 420W | 12V/9Ah | 1 | 65%~70% |
| SKP-1000A | SKP-1000A | 600W | 12V/7Ah | 2 | 70%~75% |
| SKP-1250A | SKP-1250A | 750W | 12V/7Ah | 2 | 65%~70% |
| SKP-1500A | SKP-1500A | 900W | 12V/7Ah | 2 | 70%~75% |
| SKP-2000A | SKP-2000A | 1200W | 12V/9Ah | 2 | 65%~70% |

### Conditions for setting  Present Status.

Table 5.

|  |  | HEX | USAGE (80) | Tested | Buck | Boost | Overload | Communi- cation Lost | Shutdown Imminent | Shutdown Requested | VoltageNot Regulated | Need Replacement | Remaining Time Limit Expired | Below Remaining CapacityLimit | Battery Present | ACPresent | Discharging | Charging |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  | 7 | 6 | 5 | 4 | 3 | 2 | 1 | 0 | 7 | 6 | 5 | 4 | 3 | 2 | 1 | 0 |
|  | Fully Charged BatteryLeve l= 100% |  | 0 | T* | T* | T* | T* | T* | 0 | 0 | T* | 0 | 0 | 0 | 1 | 1 | 0 | 0 |
|  | Discharging 20%  BatteryLevel  100% |  | 0 | T* | T* | T* | T* | T* | 0 | 0 | T* | 0 | 0 | 0 | 1 | 0 | 1 | 0 |
|  | Discharging 0% < BatteryLevel  20% |  | 0 | T* | T* | T* | T* | T* | 0 | 0 | T* | 0 | 1 | 0 | 1 | 0 | 1 | 0 |
|  | Fully Discharged BatteryLevel = 0% Battery Low = 0 |  | 0 | T* | T* | T* | T* | T* | 0 | 0 | T* | 0 | 1 | 1 | 1 | 0 | 1 | 0 |
|  | Fully Discharged BatteryLevel = 0% Battery Low = 1 |  | 0 | T* | T* | T* | T* | T* | 1 | 0 | T* | 1 | 1 | 1 | 1 | 0 | 0 | 0 |
|  | Charging BatteryLevel = 0% Battery Low = 1 |  | 0 | T* | T* | T* | T* | T* | 0 | 0 | T* | 1 | 1 | 1 | 1 | 1 | 0 | 1 |
|  | Charging BatteryLevel = 0% Battery Low = 0 |  | 0 | T* | T* | T* | T* | T* | 0 | 0 | T* | 0 | 1 | 1 | 1 | 1 | 0 | 1 |
|  | Charging 0% < BatteryLevel  20% |  | 0 | T* | T* | T* | T* | T* | 0 | 0 | T* | 0 | 1 | 0 | 1 | 1 | 0 | 1 |
|  | Charging 7% < BatteryLevel  99% |  | 0 | T* | T* | T* | T* | T* | 0 | 0 | T* | 0 | 0 | 0 | 1 | 1 | 0 | 1 |

T* - with Data from table 3.