Software USB communication controller

for UPS PowerCom BNT series

models BNT-400AP, BNT-500AP, BNT-600AP, BNT-800AP,

BNT-1000AP, BNT-1200AP, BNT-1500AP, BNT-2000AP, BNT-3000AP

Developer of software

research-and-production company "MES-s.r.l."

Release 1.2

October, 19, 2009

| Ver | Date | Description | Modify by |
| --- | --- | --- | --- |
| 1.0 | 07.03.2009 | New project | MES-s.r.l |
| 1.2 | 19.10.2009 | Add BNT3000 | MES-s.r.l |

Table of Contents

1.	Introduction.	2

2.	POWERCOM Communication Protocols for UPS BNT series  (models BNT-400AP, BNT-500AP, BNT-600AP, BNT-800AP, BNT-1000AP, BNT-1200AP, BNT-1500AP, BNT-2000AP, BNT-3000AP).	2

Table 2. Description of the HID Reports for PowerCom UPS-USB interface	4

Table 3. Data for Usage from UART of Power Devices PowerCom and constants.	6

Table 4. UART. Byte 12. UPS model and configuration.	10

Table 5. Conditions for setting  Present Status.	11

3.	Position of SN (serial number) in file of firmware (BNT.hex  or  BNT.rom) – OB13.	12

### Introduction.

Software USB communication controller for UPS PowerCom BNT series (model BNT-400AP, BNT-500AP, BNT-600AP, BNT-800AP, BNT-1000AP, BNT-1200AP, BNT-1500AP, BNT-2000AP, BNT-3000AP) is developed on the basis of POWERCOM UART Communication Protocols for UPS BNT series.

### POWERCOM Communication Protocols for UPS BNT series  (models BNT-400AP, BNT-500AP, BNT-600AP, BNT-800AP, BNT-1000AP, BNT-1200AP, BNT-1500AP, BNT-2000AP, BNT-3000AP).

A. General: This section specifies the UART communication protocol with main processor UPS.

B. Hardware:

Baud rate……………….. :  1200bps

Data length………………:  8 bit

Stop bits…………………:  1 bit

Parity…………………….:  None

C. Communication Protocol:

- Status Inquiry

Computer	: 1  ( binary byte)

UPS	: UPS status data stream (16 bytes). From byte 0 to byte 15 use binary data

byte  0  is load level

byte  1  is battery level

byte  2  is input voltage                 (Volt = b2*2)

byte  3  is output voltage               (Volt = b3*2)

byte  4  is input frequency

byte  5  is Firmware version

byte  6  is output frequency

byte  7  is UPS echo schedule count time high byte, minute (0..FFh)

byte  8  is UPS echo schedule count time low  byte, minute (0..FFh)

byte  9

bit 0  is line fail (1 = INV, 0 = LINE)

bit 1  is low battery (1 = BAT_ LOW, 0 = NORMAL)

bit 2  X

bit 3  AVR status  (1 = AVR,  0 = NO_AVR)

bit 4  AVR mode  (1 = BOOST,  0 = BUCK)

bit 5  Load status (1 = OVER LOAD, 0 = NORMAL)

bit 6  X

bit 7  SD mode display

byte 10

bit 0  UPS fault  (1 = FAILT)

bit 1  Battery status (1 = BAD, 0 = NORMAL)

bit 2  Test  mode  (1 = TEST, 0 = NORMAL)

bit 3  X

bit 4  Pre-SD count mode    (1 = ACTIVE)

bit 5  Schedule count mode (1 = ACTIVE)

bit 6  Disable  NO LOAD SHUTDOWN  (1 = ACTIVE)

bit 7  0

byte  11 is UPS series name

byte 12  is UPS model number and Config Voltage.

Table 1.

| High half-byte | UPS model number |  | Low half-byte | ConfigVoltage (Volt) |
| --- | --- | --- | --- | --- |
| 1 | 400VA |  | 0 | 100 |
| 2 | 500VA |  | 1 | 110 |
| 3 | 600VA |  | 2 | 115 |
| 4 | 800VA |  | 3 | 120 |
| 6 | 1000VA |  | 8 | 220 |
| 7 | 1200VA |  | 9 | 230 |
| 8 | 1500VA |  | A | 240 |
| 9 | 2000VA |  |  |  |
| B | 3000VA |  |  |  |

byte  13 is UPS echo pre-SD count time, minutes (0 – 255)

byte  14 is UPS echo pre-SD count time, seconds (0 – 59)

byte  15 is XX

- UPS self test

Computer	: 3  ( binary byte.)

UPS	: Test for 3 seconds and return to utility.

- Setup WakeUp delay

Computer	: 4, H, L  ( binary bytes)

UPS	: Preset delay for UPS output ON in shut-down (SD) mode

4  - command

H - delay time high byte, minutes (0..FFh)

L - delay time low  byte, minutes (0..FFh)

UPS in sleep mode echo status is all zero

Example: Set wakeup time 1 hour:   4 0 60

- WakeUp command

Computer	: 11  ( binary byte)

UPS	: UPS output ON in SD mode

- Control  AC NORMAL RESTART mode

Computer	: 185  ( binary byte) - enable

186  ( binary byte) - disable

- Shutdown Command

Computer	: 188, M, S  ( binary bytes)

UPS	: Shut UPS output OFF after delay

188 - command

M   - delay time, minutes (0..255)

S    - delay time, seconds (0..59)

Example: pre-shutdown counter count 1 minute and enable AC NORMAL wakeup:  185 188 1 0

- Control  NO LOAD SHUTDOWN mode (GreenMode)

Computer	: ‘G’ - enable

‘g’  - disable

### Table 2. Description of the HID Reports for PowerCom UPS-USB interface

| Report namber | Page, Usage ID | Usage Name | Data Access |
| --- | --- | --- | --- |
|  | 8404 | UPS COLLECTION (Application) |  |
|  | 8424 | PowerSummary COLLECTION (Logical) |  |
| 1 | 84FE | iProduct | R/O |
| 2 | 84FF | iSerialNumber | R/O |
| 3 | 84FD | iManufacturer | R/O |
| 4 | 858F | iOEMInformation | R/O |
| 5 | 8589 | iDeviceChemistery | R/O |
| 7 | 858B | Rechargable | R/O |
| 8 | 852C | CapacityMode | R/O |
| 9 | 8583 | DesignCapacity * | R/O |
|  | 8567 | FullChargeCapacity * |  |
| 10 | 8566 | RemainingCapacity | R/O |
| 11 | 858C | WarningCapacityLimit | R/O |
| 12 | 8529 | RemainingCapacityLimit | R/O |
| 13 | 8585 | ManufacturerDate | R/O |
| 14 | 8568 | RunTimeToEmpty | R/O |
| 15 | 8457 | DelayBeforeShutdown | R/W |
| 16 | 8456 | DelayBeforeStartup | R/W |
| 17 | 8440 | ConfigVoltage | R/O |
| 18 | 8430 | Voltage | R/O |
| 19 | 845A | AudibleAlarmControl | R/O |
| 20 | 8402 | PresentStatus COLLECTION (Logical) | R/O |
|  |  | Collection multi-bits Report ** |  |
|  | 8544 | Charging |  |
|  | 8545 | Discharging |  |
|  | 85D0 | ACPresent |  |
|  | 85D1 | BatteryPresent |  |
|  | 8542 | BelowRemainingCapacityLimit ** |  |
|  | 8543 | RemainingTimeLimitExpired ** |  |
|  | 854B | NeedReplacement |  |
|  | 85DB | VoltageNotRegulated ** |  |
|  | 8468 | ShutdownRequested ** |  |
|  | 8469 | ShutdownImminent |  |
|  | 8473 | CommunicationLost |  |
|  | 8465 | Overload |  |
|  |  | COUNT (3) ** |  |
|  | 8680 | Usage (80) from Usage_Page (86) ** |  |
|  |  | END_COLLECTION [PresentStatus, Logical] |  |
|  |  | END_COLLECTION [PoweSummary, Logical] |  |
|  | 8412 | Battery COLLECTION (Physical) |  |
| 21 | 8458 | Test | R/W |
| 22 | 8470 | Initialized | W/O |
| 23 | 8585 | ManufacturerDate | R/O |
| 24 | 8566 | RemainingCapacity | R/O |
| 25 | 8440 | ConfigVoltage | R/O |
| 26 | 8430 | Voltage | R/O |
| 27 | 8456 | DelayBeforeStartup | R/W |
|  |  | END_COLLECTION [Battery, Physical] |  |
|  | 841A | Input COLLECTION (Physical) |  |
| 28 | 8440 | ConfigVoltage | R/O |
| 29 | 8430 | Voltage | R/O |
| 30 | 8432 | Frequency | R/O |
|  |  | END_COLLECTION [Input, Physical] |  |
|  | 841C | Output COLLECTION (Physical) |  |
| 31 | 8435 | PercentLoad | R/O |
| 32 | 8440 | ConfigVoltage | R/O |
| 33 | 8430 | Voltage | R/O |
| 34 | 8432 | Frequency | R/O |
| 35 | 8457 | DelayBeforeShutdown | R/W |
| 36 | 8456 | DelayBeforeStartup | R/W |
|  |  | END_COLLECTION [Output, Physical] |  |
| 6 | 8401 | iName | R/O |
| 37 | 845A | Audible Alarm Control | R/O |
| 38 | 8402 | Present Status COLLECTION (Logical) | R/O |
|  |  | Collection multi-bits Report |  |
|  | 8544 | Charging |  |
|  | 8545 | Discharging |  |
|  | 85D0 | ACPresent |  |
|  | 85D1 | BatteryPresent |  |
|  | 8542 | BelowRemainingCapacityLimit ** |  |
|  | 8543 | RemainingTimeLimitExpired ** |  |
|  | 854B | NeedReplacement |  |
|  | 85DB | VoltageNotRegulated ** |  |
|  | 8468 | ShutdownRequested ** |  |
|  | 8469 | ShutdownImminent |  |
|  | 8473 | CommunicationLost |  |
|  | 8465 | Overload |  |
|  | 846E | Boost |  |
|  | 846F | Buck |  |
|  | 8471 | Tested |  |
|  | 8680 | Usage(80) from Usage_Page (86) ** |  |
|  |  | END_COLLECTION [PresentStatus, Logical] |  |
| 39 | 8469 | ShutdownImminent | R/W |
|  |  | END_COLLECTION [UPS, Application] |  |

*)   - two Usage in one report.

**) - Not to use. For compatibility with system driver.

Table 2.a. Not standard Usages.

| String number | Usage Name | Data Access |
| --- | --- | --- |
| 100 | Usage ReadUART | R/O |

### Table 3. Data for Usage from UART of Power Devices PowerCom and constants.

System requests for usage with Microsoft UPS system driver

(first Byte is Byte 0 )

| Report number | Page, Usage ID | Usage Name | Data Access | Data | Length |
| --- | --- | --- | --- | --- | --- |
|  | 8424 | PowerSummary COLLECTION |  |  |  |
| 1 | 84FE | iProduct | R/O | UPS BNT-ХХХХAP FW5.A6 ХХХХ - Model number from table 4 | 60 Byte |
| 2 | 84FF | iSerialNumber | R/O | 0A6-0000-0001 | 32 Byte |
| 3 | 84FD | iManufacturer | R/O | POWERCOM Co.,LTD | 34 Byte |
| 4 | 858F | iOEMInformation | R/O | POWERCOM Co.,LTD | 34 Byte |
| 5 | 8589 | iDeviceChemistery | R/O | PbAc | 10 Byte |
| 7 | 858B | Rechargable | R/O | 1 | 1 Byte |
| 8 | 852C | CapacityMode | R/O | 2 (%) | 1 Byte |
| 9 | 8583 | Designcapacity* | R/O | 100 (in %) | 2 Byte |
|  | 8567 | FullChargeCapacity * |  | 100 (in %) |  |
| 10 | 8566 | RemainingCapacity | R/O | Byte 1 "battery level" (in %) | 1 Byte |
| 11 | 858C | WarningCapacityLimit | R/O | 30 (in %) | 1 Byte |
| 12 | 8529 | RemainingCapacityLimit | R/O | Initially 10 (in %), is it hereinafter assigned by system driver | 1 Byte |
| 13 | 8585 | ManufacturerDate | R/O | ( Year-1980 ) * 512 + Month * 32 + Day | 2 Byte |
| 14 | 8568 | RunTimeToEmpty | R/O | It Is Calculated on the grounds of Byte 0, Byte 1, Byte 12, ( in sec ) Calculated in table T =( ( Caccum * K * BatteryLevel * 60 min ) / ( Pnom * LoadLevel ) ) * 60 Unit Caccum – 2%, Unit LoadLevel – 16%, | 2 Byte |
| 15 | 8457 | DelayBeforeShutdown *** | R/W | Read: Byte 13, Byte 14 (min, sec) Write: If Byte(sec), bit7=0 and bit6=0 Then If Byte 9, bit0=1 Then command 185, 188, min, sec If Byte 9, bit0=0 Then command 186, 188, min, sec If Byte(sec), bit7=0 and bit6=1 Then command 185, 188, min, sec If Byte(sec), bit7=1 and bit6=0 Then Then command 186, 188, min, sec If Byte(sec), bit7=1 and bit6=1 Then No actions | 2 Byte |
| 16 | 8456 | DelayBeforeStartup *** | R/W | Read: Byte 7, byte 8 (min) Write: Command 4, high byte min, low byte min | 2 Byte |
| 17 | 8440 | ConfigVoltage | R/O | from Byte 12 (see table 3) | 1 Byte |
| 18 | 8430 | Voltage | R/O | Byte 3 " output Voltage " | 2 Byte |
| 19 | 845A | AudibleAlarmControl | R/O | If Byte 10, bit3=1 Then value =2 If Byte 10, bit3=0 Then value =1 | 1 Byte |
|  | 8412 | Battery COLLECTION |  |  |  |
| 21 | 8458 | Test | R/W | Read: If Byte 10 bit1=0 AND bit2=0 Then value = 1 (“Done and Passed”) If Byte 10 bit1 =1 AND bit2=0 Then value = 3 (“Done and Error”) If Byte 10 bit2 =1 Then value = 5 (“Test in progress”) Write : If value =2 Then command 3 , If value<>2 Then “No test” | 1 Byte |
| 22 | 8470 | Initialized | W/O | Write : If value =1 Then command 11 , Else Not command | 1 Byte |
| 23 | 8585 | ManufacturerDate | R/O | ( Year-1980 ) * 512 + Month * 32 + Day | 2 Byte |
| 24 | 8566 | RemainingCapacity | R/O | Byte 1 " battery level " (in %) | 1 Byte |
| 25 | 8440 | ConfigVoltage | R/O | from Byte 12 (see table 3) (in Volt) | 1 Byte |
| 26 | 8430 | Voltage | R/O | Byte 3 "output Voltage" (in Volt) | 2 Byte |
| 27 | 8456 | DelayBeforeStartup *** | R/W | Similary Report number 16 | 2 Byte |
|  | 841A | Input COLLECTION |  |  |  |
| 28 | 8440 | ConfigVoltage | R/O | from Byte 12 (see table 3) (in Volt) | 1 Byte |
| 29 | 8430 | Voltage | R/O | Byte 2 "input Voltage" (in Volt) | 2 Byte |
| 30 | 8432 | Frequency | R/O | Byte 4 "input Frequency" (in Hz) | 1 Byte |
|  | 841C | Output COLLECTION |  |  |  |
| 31 | 8435 | PercentLoad | R/O | Byte 0 "load level" (in %) | 1 Byte |
| 32 | 8440 | ConfigVoltage | R/O | from Byte 12 (see table 3) (in Volt) | 1 Byte |
| 33 | 8430 | Voltage | R/O | Byte 3 "output Voltage" (in Volt) | 2 Byte |
| 34 | 8432 | Frequency | R/O | Byte 6 "output Frequency" (in Hz) | 1 Byte |
| 35 | 8457 | DelayBeforeShutdown *** | R/W | similarly Report number 15 | 2 Byte |
| 36 | 8456 | DelayBeforeStartup *** | R/W | similarly Report number 16 | 2 Byte |
| 6 | 8401 | iName | R/O | POWERCOM USB UPS | 34 Byte |
| 37 | 845A | Audible Alarm Control | R/O | If Byte 10, bit3=1 Then value =2 If Byte 10, bit3=0 Then value =1 | 1 Byte |
|  | 8402 | Present Status COLLECTION |  |  |  |
| 38 |  | Collection multi-bits Report | R/O |  | 2 Byte |
|  | 8544 | Charging |  | (see table 4) |  |
|  | 8545 | Discharging |  | (see table 4) |  |
|  | 85D0 | ACPresent |  | Byte 9, Not bit0 |  |
|  | 85D1 | BatteryPresent |  | (see table 4) |  |
|  | 8542 | BelowRemainingCapacityLimit ** |  | (see table 4) |  |
|  | 8543 | RemainingTimeLimitExpired ** |  | (see table 4) |  |
|  | 854B | NeedReplacement |  | (see table 4) |  |
|  | 85DB | VoltageNotRegulated |  | Byte 10, bit0 |  |
|  | 8468 | ShutdownRequested ** |  | 0 |  |
|  | 8469 | ShutdownImminent |  | IF Byte 10, bit6=0 and [Byte 0]=0 Then value =1 |  |
|  | 8473 | CommunicationLost |  | IF Error UART Then value =1 |  |
|  | 8465 | Overload |  | Byte 9, bit5 |  |
|  | 846E | Boost |  | Byte 9, If bit3=1 then value=bit4, If bit3=0 Then value=0 |  |
|  | 846F | Buck |  | Byte 9, If bit3=1 then value= Not bit4, If bit3=0 Then value=0 |  |
|  | 8471 | Tested |  | Byte 10, bit2 |  |
| 39 | 8469 | ShutdownImminent | R/W | Read: Byte 10, bit6 Write: If value=1 Then command “G” Else command “g” | 1 Byte |

| String number | Usage Name | Data Access | Data | Lengh |
| --- | --- | --- | --- | --- |
| 100 | Usage ReadUART | R/O | Read data from UART (Byte 0  Byte 15) | 16 Byte |

*)   - two Usage in one report.

**) - Not to use. For compatibility with system driver.

***) - Does not correspond to the standard "Universal Serial Bus Usage Tables for HID Power Devices". Productivity microcontroller CY7C63723 is not

sufficient, that real-time to execute transformations data.

****) - string variable are sent in format UNICOD

### Table 4. UART. Byte 12. UPS model and configuration.

Data from the table are used for calculation RunTimeToEmpty in the tabular form.

Higher part of the byte 12 - UPS model, Pnom and Design Capacity, Number Acc, Efficiency

| UPS_Model | High half-byte of the byte 12 | Pnom (VA) | DesignCapacity (A/H) | Number Acc. | Efficiency Inverter (%) |
| --- | --- | --- | --- | --- | --- |
| BNT-400AP | 1X | 400 | 12V-7.2AH | 1 | 70~80 |
| BNT-500AP | 2X | 500 | 12V-7.2AH | 1 | 70~80 |
| BNT-600AP | 3X | 600 | 12V-7.2AH | 1 | 70~80 |
| BNT-800AP | 4X | 800 | 12V-9.0AH | 1 | 70~80 |
| BNT-1000AP | 6X | 1000 | 12V-7.2AH | 2 | 70~80 |
| BNT-1200AP | 7X | 1200 | 12V-7.2AH | 2 | 70~80 |
| BNT-1500AP | 8X | 1500 | 12V-7.2AH | 2 | 70~80 |
| BNT-2000AP | 9X | 2000 | 12V-9.0AH | 2 | 70~80 |
| BNT-3000AP | BX | 3000 | 12V-9.0AH | 3 | 70~80 |

### Table 5. Conditions for setting  Present Status.

|  |  | HEX | USAGE (80) | Tested | Buck | Boost | Overload | Communi cation Lost | Shutdown Imminent | Shutdown Requested | VoltageNot Regulated | Need Replacement | Remaining Time Limit Expired | Below Remaining CapacityLimit | Battery Present | ACPresent | Discharging | Charging |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  | 7 | 6 | 5 | 4 | 3 | 2 | 1 | 0 | 7 | 6 | 5 | 4 | 3 | 2 | 1 | 0 |
|  | Fully Charged Byte 9, bit0 =0 BatteryLeve l= 100% | XX 0C | T* | T* | T* | T* | T* | T* | T* | T* | T* | 0 | 0 | 0 | 1 | T* | 0 | 0 |
|  | Discharging Byte 9, bit0 = 1 10%  BatteryLevel  100% | XX 0A | T* | T* | T* | T* | T* | T* | T* | T* | T* | 0 | 0 | 0 | 1 | T* | 1 | 0 |
|  | Discharging Byte 9, bit0 = 1 0% < BatteryLevel  10% | XX 2A | T* | T* | T* | T* | T* | T* | T* | T* | T* | 0 | 1 | 0 | 1 | T* | 1 | 0 |
|  | Fully Discharged Byte 9, bit0 = 1; Byte 9, bit1 = 0 BatteryLevel = 0% | XX 3A | T* | T* | T* | T* | T* | T* | T* | T* | T* | 0 | 1 | 1 | 1 | T* | 1 | 0 |
|  | Fully Discharged Byte 9, bit0 = 1; Byte 9, bit1 = 1 BatteryLevel = 0% | XX 78 | T* | T* | T* | T* | T* | T* | T* | T* | T* | 1 | 1 | 1 | 1 | T* | 0 | 0 |
|  | Charging Byte 9, bit0 = 0; Byte 9, bit1 = 1 BatteryLevel = 0% | XX 7D | T* | T* | T* | T* | T* | T* | T* | T* | T* | 1 | 1 | 1 | 1 | T* | 0 | 1 |
|  | Charging Byte 9, bit0 = 0; Byte 9, bit1 = 0 BatteryLevel = 0% | XX 3D | T* | T* | T* | T* | T* | T* | T* | T* | T* | 0 | 1 | 1 | 1 | T* | 0 | 1 |
|  | Charging Byte 9, bit0 = 0 0% < BatteryLevel  7% | XX 2D | T* | T* | T* | T* | T* | T* | T* | T* | T* | 0 | 1 | 0 | 1 | T* | 0 | 1 |
|  | Charging Byte 9, bit0 = 0 7% < BatteryLevel  99% | XX 0D | T* | T* | T* | T* | T* | T* | T* | T* | T* | 0 | 0 | 0 | 1 | T* | 0 | 1 |

T*) – from Table 2. Data for Usage from UART of Power Devices PowerCom and constants.

### Position of SN (serial number) in file of firmware (BNT.hex  or  BNT.rom) – OB13.

Fragment of listing below:

0B11              iserialnumber_string:                 ; Serial Number String

0B11 20    [00]     db  20h

0B12 03    [00]     db  3

0B13 30 00 ...      dsu "0A6-0000-0001  "