Software USB communication controller

for UPS PowerCom IMPERIAL series

Developer of software

research-and-production company "MES-s.r.l."

Release 2.1

March 7, 2008

Table of Contents

Table 1. Description of the HID Reports for PowerCom UPS-USB interface	2

Table 2. Data for Usage from UART of Power Devices PowerCom and constants.	4

Table 3. UART. Byte 12. UPS model.	8

Table 4. Conditions for setting  Present Status.	9

Position of SN (serial number) in file of firmware (PCM.hex  or  PCM.rom) – OB13.	10

### Table 1. Description of the HID Reports for PowerCom UPS-USB interface

| Report namber | Page, Usage ID | Usage Name | Data Access |
| --- | --- | --- | --- |
|  | 8404 | UPS COLLECTION (Application) |  |
|  | 8424 | PowerSummary COLLECTION (Logical) |  |
| 1 | 84FE | iProduct | R/O |
| 2 | 84FF | iSerialNumber | R/O |
| 3 | 84FD | iManufacturer | R/O |
| 4 | 858F | iOEMInformation | R/O |
| 5 | 8589 | iDeviceChemistery | R/O |
| 7 | 858B | Rechargable | R/O |
| 8 | 852C | CapacityMode | R/O |
| 9 | 8583 | DesignCapacity * | R/O |
|  | 8567 | FullChargeCapacity * |  |
| 10 | 8566 | RemainingCapacity | R/O |
| 11 | 858C | WarningCapacityLimit | R/O |
| 12 | 8529 | RemainingCapacityLimit | R/O |
| 13 | 8585 | ManufacturerDate | R/O |
| 14 | 8568 | RunTimeToEmpty | R/O |
| 15 | 8457 | DelayBeforeShutdown | R/W |
| 16 | 8456 | DelayBeforeStartup | R/W |
| 17 | 8440 | ConfigVoltage | R/O |
| 18 | 8430 | Voltage | R/O |
| 19 | 845A | AudibleAlarmControl | R/O |
| 20 | 8402 | PresentStatus COLLECTION (Logical) | R/O |
|  |  | Collection multi-bits Report ** |  |
|  | 8544 | Charging |  |
|  | 8545 | Discharging |  |
|  | 85D0 | ACPresent |  |
|  | 85D1 | BatteryPresent |  |
|  | 8542 | BelowRemainingCapacityLimit ** |  |
|  | 8543 | RemainingTimeLimitExpired ** |  |
|  | 854B | NeedReplacement |  |
|  | 85DB | VoltageNotRegulated ** |  |
|  | 8468 | ShutdownRequested ** |  |
|  | 8469 | ShutdownImminent |  |
|  | 8473 | CommunicationLost |  |
|  | 8465 | Overload |  |
|  |  | COUNT (3) ** |  |
|  | 8680 | Usage (80) from Usage_Page (86) ** |  |
|  |  | END_COLLECTION [PresentStatus, Logical] |  |
|  |  | END_COLLECTION [PoweSummary, Logical] |  |
|  | 8412 | Battery COLLECTION (Physical) |  |
| 21 | 8458 | Test | R/W |
| 22 | 8470 | Initialized | W/O |
| 23 | 8585 | ManufacturerDate | R/O |
| 24 | 8566 | RemainingCapacity | R/O |
| 25 | 8440 | ConfigVoltage | R/O |
| 26 | 8430 | Voltage | R/O |
| 27 | 8456 | DelayBeforeStartup | R/W |
|  |  | END_COLLECTION [Battery, Physical] |  |
|  | 841A | Input COLLECTION (Physical) |  |
| 28 | 8440 | ConfigVoltage | R/O |
| 29 | 8430 | Voltage | R/O |
| 30 | 8432 | Frequency | R/O |
|  |  | END_COLLECTION [Input, Physical] |  |
|  | 841C | Output COLLECTION (Physical) |  |
| 31 | 8435 | PercentLoad | R/O |
| 32 | 8440 | ConfigVoltage | R/O |
| 33 | 8430 | Voltage | R/O |
| 34 | 8432 | Frequency | R/O |
| 35 | 8457 | DelayBeforeShutdown | R/W |
| 36 | 8456 | DelayBeforeStartup | R/W |
|  |  | END_COLLECTION [Output, Physical] |  |
| 6 | 8401 | iName | R/O |
| 37 | 845A | Audible Alarm Control | R/O |
| 38 | 8402 | Present Status COLLECTION (Logical) | R/O |
|  |  | Collection multi-bits Report |  |
|  | 8544 | Charging |  |
|  | 8545 | Discharging |  |
|  | 85D0 | ACPresent |  |
|  | 85D1 | BatteryPresent |  |
|  | 8542 | BelowRemainingCapacityLimit ** |  |
|  | 8543 | RemainingTimeLimitExpired ** |  |
|  | 854B | NeedReplacement |  |
|  | 85DB | VoltageNotRegulated ** |  |
|  | 8468 | ShutdownRequested ** |  |
|  | 8469 | ShutdownImminent |  |
|  | 8473 | CommunicationLost |  |
|  | 8465 | Overload |  |
|  | 846E | Boost |  |
|  | 846F | Buck |  |
|  | 8471 | Tested |  |
|  | 8680 | Usage(80) from Usage_Page (86) ** |  |
|  |  | END_COLLECTION [PresentStatus, Logical] |  |
| 39 | 8469 | ShutdownImminent | R/W |
|  |  | END_COLLECTION [UPS, Application] |  |

*)   - two Usage in one report.

**) - Not to use. For compatibility with system driver.

Table 1.a. Not standard Usages.

| String number | Usage Name | Data Access |
| --- | --- | --- |
| 100 | Usage ReadUART | R/O |

### Table 2. Data for Usage from UART of Power Devices PowerCom and constants.

System requests for usage with Microsoft UPS system driver

(first Byte is Byte 0 )

| Report number | Page, Usage ID | Usage Name | Data Access | Data | Length |
| --- | --- | --- | --- | --- | --- |
|  | 8424 | PowerSummary COLLECTION |  |  |  |
| 1 | 84FE | iProduct | R/O | UPS IMP-ХХХХAP FW1.A0 ХХХХ - Model number from table 3 | 60 Byte |
| 2 | 84FF | iSerialNumber | R/O | 0A2-0000-0001 | 32 Byte |
| 3 | 84FD | iManufacturer | R/O | POWERCOM Co.,LTD | 34 Byte |
| 4 | 858F | iOEMInformation | R/O | POWERCOM Co.,LTD | 34 Byte |
| 5 | 8589 | iDeviceChemistery | R/O | PbAc | 10 Byte |
| 7 | 858B | Rechargable | R/O | 1 | 1 Byte |
| 8 | 852C | CapacityMode | R/O | 2 (%) | 1 Byte |
| 9 | 8583 | Designcapacity* | R/O | 100 (in %) | 2 Byte |
|  | 8567 | FullChargeCapacity * |  | 100 (in %) |  |
| 10 | 8566 | RemainingCapacity | R/O | Byte 1 "battery level" (in %) | 1 Byte |
| 11 | 858C | WarningCapacityLimit | R/O | 30 (in %) | 1 Byte |
| 12 | 8529 | RemainingCapacityLimit | R/O | Initially 10 (in %), is it hereinafter assigned by system driver | 1 Byte |
| 13 | 8585 | ManufacturerDate | R/O | ( Year-1980 ) * 512 + Month * 32 + Day | 2 Byte |
| 14 | 8568 | RunTimeToEmpty | R/O | It Is Calculated on the grounds of Byte 0, Byte 1, Byte 12, ( in sec ) Calculated in table T =( ( Caccum * K * BatteryLevel * 60 min ) / ( Pnom * LoadLevel ) ) * 60 Where K =9,6 for Imp425-Imp825 K =19,2 for Imp1025-Imp2000 Unit Caccum – 4%, Unit LoadLevel – 16%, | 2 Byte |
| 15 | 8457 | DelayBeforeShutdown *** | R/W | Read: Byte 13, Byte 14 (min, sec) Write: Two free senior bits of byte of seconds are used for possibility of a choice of a prefix-command before 188 command performance If Byte(sec), bit7=0 and bit6=0 Then If Byte 9, bit0=1 Then command 185, 188, min, sec If Byte 9, bit0=0 Then command 186, 188, min, sec If Byte(sec), bit7=0 and bit6=1 Then command 185, 188, min, sec If Byte(sec), bit7=1 and bit6=0 Then Then command 186, 188, min, sec If Byte(sec), bit7=1 and bit6=1 Then No actions | 2 Byte |
| 16 | 8456 | DelayBeforeStartup *** | R/W | Read: Byte 7, byte 8 (min) Write: Command 4, high byte min, low byte min | 2 Byte |
| 17 | 8440 | ConfigVoltage | R/O | from Byte 12 (see table 3) | 1 Byte |
| 18 | 8430 | Voltage | R/O | Byte 3 " output Voltage " | 2 Byte |
| 19 | 845A | AudibleAlarmControl | R/O | If Byte 10, bit3=1 Then value =2 If Byte 10, bit3=0 Then value =1 | 1 Byte |
|  | 8412 | Battery COLLECTION |  |  |  |
| 21 | 8458 | Test | R/W | Read: If Byte 10 bit1=0 AND bit2=0 Then value = 1 (“Done and Passed”) If Byte 10 bit1 =1 AND bit2=0 Then value = 3 (“Done and Error”) If Byte 10 bit2 =1 Then value = 5 (“Test in progress”) Write : If value =1 Then command 3 , If value<>1 Then “No test” | 1 Byte |
| 22 | 8470 | Initialized | W/O | Write : If value =1 Then command 11 , Else Not command | 1 Byte |
| 23 | 8585 | ManufacturerDate | R/O | ( Year-1980 ) * 512 + Month * 32 + Day | 2 Byte |
| 24 | 8566 | RemainingCapacity | R/O | Byte 1 " battery level " (in %) | 1 Byte |
| 25 | 8440 | ConfigVoltage | R/O | from Byte 12 (see table 3) (in Volt) | 1 Byte |
| 26 | 8430 | Voltage | R/O | Byte 3 "output Voltage" (in Volt) | 2 Byte |
| 27 | 8456 | DelayBeforeStartup *** | R/W | Similary Report number 16 | 2 Byte |
|  | 841A | Input COLLECTION |  |  |  |
| 28 | 8440 | ConfigVoltage | R/O | from Byte 12 (see table 3) (in Volt) | 1 Byte |
| 29 | 8430 | Voltage | R/O | Byte 2 "input Voltage" (in Volt) | 2 Byte |
| 30 | 8432 | Frequency | R/O | Byte 4 "input Frequency" (in Hz) | 1 Byte |
|  | 841C | Output COLLECTION |  |  |  |
| 31 | 8435 | PercentLoad | R/O | Byte 0 "load level" (in %) | 1 Byte |
| 32 | 8440 | ConfigVoltage | R/O | from Byte 12 (see table 3) (in Volt) | 1 Byte |
| 33 | 8430 | Voltage | R/O | Byte 3 "output Voltage" (in Volt) | 2 Byte |
| 34 | 8432 | Frequency | R/O | Byte 6 "output Frequency" (in Hz) | 1 Byte |
| 35 | 8457 | DelayBeforeShutdown *** | R/W | similarly Report number 15 | 2 Byte |
| 36 | 8456 | DelayBeforeStartup *** | R/W | similarly Report number 16 | 2 Byte |
| 6 | 8401 | iName | R/O | POWERCOM USB UPS | 34 Byte |
| 37 | 845A | Audible Alarm Control | R/O | If Byte 10, bit3=1 Then value =2 If Byte 10, bit3=0 Then value =1 | 1 Byte |
|  | 8402 | Present Status COLLECTION |  |  |  |
| 38 |  | Collection multi-bits Report | R/O |  | 2 Byte |
|  | 8544 | Charging |  | (see table 4) |  |
|  | 8545 | Discharging |  | (see table 4) |  |
|  | 85D0 | ACPresent |  | Byte 9, Not bit0 |  |
|  | 85D1 | BatteryPresent |  | (see table 4) |  |
|  | 8542 | BelowRemainingCapacityLimit ** |  | (see table 4) |  |
|  | 8543 | RemainingTimeLimitExpired ** |  | (see table 4) |  |
|  | 854B | NeedReplacement |  | (see table 4) |  |
|  | 85DB | VoltageNotRegulated |  | Byte 10, bit0 |  |
|  | 8468 | ShutdownRequested ** |  | 0 |  |
|  | 8469 | ShutdownImminent |  | IF Byte 10, bit6=0 and [Byte 0]=0 Then value =1 |  |
|  | 8473 | CommunicationLost |  | IF Error UART Then value =1 |  |
|  | 8465 | Overload |  | Byte 9, bit5 |  |
|  | 846E | Boost |  | Byte 9, If bit3=1 then value=bit4, If bit3=0 Then value=0 |  |
|  | 846F | Buck |  | Byte 9, If bit3=1 then value= Not bit4, If bit3=0 Then value=0 |  |
|  | 8471 | Tested |  | Byte 10, bit2 |  |
| 39 | 8469 | ShutdownImminent | R/W | Read: IF [Byte 10, bit6=0] and [Byte 9, bit0=1] and [Byte 0]=0 Then value =1 In all other cases value = 0 Write: If value=1 Then command “G” Else command “g” | 1 Byte |

| String number | Usage Name | Data Access | Data | Lengh |
| --- | --- | --- | --- | --- |
| 100 | Usage ReadUART | R/O | Read data from UART (Byte 0  Byte 15) | 16 Byte |

*)   - two Usage in one report.

**) - Not to use. For compatibility with system driver.

***) - Does not correspond to the standard "Universal Serial Bus Usage Tables for HID Power Devices". Productivity microcontroller CY7C63723 is not

sufficient, that real-time to execute transformations data.

****) - string variable are sent in format UNICOD

### Table 3. UART. Byte 12. UPS model.

higher part of the byte - UPS model, Pnom and Design Capacity,

| higher part of the byte | Model | Model number | Pnom (Wt) | DesignCapacity (A/H) | Number Acc. |
| --- | --- | --- | --- | --- | --- |
| 1 | Imp-425 | -425 | 425 | 7 | 1 |
| 2 | Imp-525 | -525 | 525 | 7 | 1 |
| 3 | Imp-625 | -625 | 625 | 7 | 1 |
| 4 | Imp-825 | -825 | 825 | 9 | 1 |
| 5 |  |  |  |  |  |
| 6 | Imp-1025 | 1025 | 1025 | 7 | 2 |
| 7 | Imp-1200 | 1200 | 1200 | 7 | 2 |
| 8 | Imp-1500 | 1500 | 1500 | 7 | 2 |
| A | Imp-2000 | 2000 | 2000 | 9 | 2 |

lower part of the byte - Config Voltage.

| lower part of the byte | ConfigVoltage (Volt) |
| --- | --- |
| 0 | 100 |
| 1 | 110 |
| 2 | 115 |
| 3 | 120 |
| 8 | 220 |
| 9 | 230 |
| A | 240 |

### Table 4. Conditions for setting  Present Status.

|  |  | HEX | USAGE (80) | Tested | Buck | Boost | Overload | Communi cation Lost | Shutdown Imminent | Shutdown Requested | VoltageNot Regulated | Need Replacement | Remaining Time Limit Expired | Below Remaining CapacityLimit | Battery Present | ACPresent | Discharging | Charging |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  | 7 | 6 | 5 | 4 | 3 | 2 | 1 | 0 | 7 | 6 | 5 | 4 | 3 | 2 | 1 | 0 |
|  | Fully Charged Byte 9, bit0 =0 BatteryLeve l= 100% | XX 0C | T* | T* | T* | T* | T* | T* | T* | T* | T* | 0 | 0 | 0 | 1 | T* | 0 | 0 |
|  | Discharging Byte 9, bit0 = 1 10%  BatteryLevel  100% | XX 0A | T* | T* | T* | T* | T* | T* | T* | T* | T* | 0 | 0 | 0 | 1 | T* | 1 | 0 |
|  | Discharging Byte 9, bit0 = 1 0% < BatteryLevel  10% | XX 2A | T* | T* | T* | T* | T* | T* | T* | T* | T* | 0 | 1 | 0 | 1 | T* | 1 | 0 |
|  | Fully Discharged Byte 9, bit0 = 1; Byte 9, bit1 = 0 BatteryLevel = 0% | XX 3A | T* | T* | T* | T* | T* | T* | T* | T* | T* | 0 | 1 | 1 | 1 | T* | 1 | 0 |
|  | Fully Discharged Byte 9, bit0 = 1; Byte 9, bit1 = 1 BatteryLevel = 0% | XX 78 | T* | T* | T* | T* | T* | T* | T* | T* | T* | 1 | 1 | 1 | 1 | T* | 0 | 0 |
|  | Charging Byte 9, bit0 = 0; Byte 9, bit1 = 1 BatteryLevel = 0% | XX 7D | T* | T* | T* | T* | T* | T* | T* | T* | T* | 1 | 1 | 1 | 1 | T* | 0 | 1 |
|  | Charging Byte 9, bit0 = 0; Byte 9, bit1 = 0 BatteryLevel = 0% | XX 3D | T* | T* | T* | T* | T* | T* | T* | T* | T* | 0 | 1 | 1 | 1 | T* | 0 | 1 |
|  | Charging Byte 9, bit0 = 0 0% < BatteryLevel  7% | XX 2D | T* | T* | T* | T* | T* | T* | T* | T* | T* | 0 | 1 | 0 | 1 | T* | 0 | 1 |
|  | Charging Byte 9, bit0 = 0 7% < BatteryLevel  99% | XX 0D | T* | T* | T* | T* | T* | T* | T* | T* | T* | 0 | 0 | 0 | 1 | T* | 0 | 1 |

T*) – from Table 2. Data for Usage from UART of Power Devices PowerCom and constants.

### Position of SN (serial number) in file of firmware (PCM.hex  or  PCM.rom) – OB13.

Fragment of listing below:

0B11              iserialnumber_string:                 ; Serial Number String

0B11 20    [00]     db  20h

0B12 03    [00]     db  3

0B13 30 00 ...      dsu "0A2-0000-0001  "